## Cover sheet
Victoria over-capacity review
Is over-capacity the reason for low augmentation levels in Victoria?
2012-08-03
Nuttall Consulting does not take responsibility in any way whatsoever to any person or organisation other than the AEMO in respect of information set out in this document, including any errors or omissions therein, arising through negligence or otherwise.
Overview:
This workbook supports the analysis and charting provided in the Nuttall Consulting report "Victoria over-capacity review: Is over-capacity the reason for low augmentation levels in Victoria?", dated 27 July 2012. This report contains details of the data and underlying calculations contained in this workbook.
Caution: This workbook is not protected and so any changes could affect the calculations

## Guide
Utilisation metric overview
The workbook summarises the calculation of the utilisation metrics discussed in the report. The form and rationale for these metrics is discussed in Section 3 of the report. Sections 5 and 6 of the report provide more detailed explanations of the underlying data, assumptions and calculations that are provided in this workbook. The following is a brief summary of the metrics.
The utilisation metric is defined to reflect the average utilisation across a population of assets in each region. The utilisation (as defined in the report) of any individual asset is taken to be its loading at the time of regional peak demand as a percentage of its continuous thermal rating at that time.
Two metrics are used to reflect the two main network planning components: transformers and lines . A weighted average across the population of components is used to account for the scale of the individual components in each category. For each transformer, its rating is used as the weighting. For each line, its rating multiplied by its length is used.
The utilisation metrics for these two components are also broken down into the following categories:
- Transformers: tie transformers and terminal stations (or connection points)
- Lines: by nominal voltage (500 kV, 330 kV, 275 kV, 220 kV, 132 kV, 110 kV, 66 kV)
(the category "all" signifies all elements in the overall transformer or line component)
Structure of workbook
Regional data sheets
The workbook contains three Regional data sheets, called VIC, NSW, QLD. These can be identified by the blue tab shading.
These three sheets contain the data and calculations specific to each of the three regions in the study. The sheets contain references to the relevant report sections where data, assumptions and calculations are discussed.
Each sheet has the same structure, consisting of two main tables:
The first table, "Utilisation summary data for report charting", contains the utilisations metrics and other supporting data that is used for charting purposes. The table can be considered in two sections
The first section (from row 4 to row 58) contains the actual data that is extracted from the 18 AEMO OPDMS data files (see S5.1 of the report). This data includes the utilisation metrics (based upon the actual data), and underlying data, including aggregate loading and ratings, etc. Headings and comments in this table provide descriptions of the data that is extracted; however, readers are referred to section 5.1 of the report for a more complete discussion.
The second section (from row 59 to row 67) summarises the corrected utilisation metrics (discussed in Sections 5.2, 5.3 and 6.1 of the report).
The second table, "S5.2, S5.3 & S6 - calculations and supporting data", contains the data, assumptions and calculations that are applied to calculate the corrected utilisation metrics provided in the first table (noted above). Headings, comments and the underlying formulas in this table provide descriptions of the data and calculations; however, readers are referred to sections 5.2, 5.3 and 6 of the report for a more complete discussion (references to relevant report sections are included in the table).
Utilisation charting
The workbook contains one sheet, called Utilisation charting, that contains the charts that are provided in the report. This sheet can be identified by the red tab shading.
This sheet is structured as follows:
The table between row 1 and row 31 contains consolidated data from each of the three regional data sheets. This is the data that is charted. The data includes:
The annual trends in the utilisation metrics (both actual and corrected) for each region - in column C to column N.
The average corrected utilisation metrics and density measures, discussed in Section 6.2 of the report - in column O to column T.
The table between row 33 and row 16 contains the charts that are provided in the report. These charts link to the data table above. Each chart has a heading and reference to the relevant section in the report. This report section should be referred to in order to obtain a more complete explanation of the chart.
Importantly, cell S98 in the charting table includes a toggle to change the corrected data and charts to either include or exclude the corrections discussed in Section 6 of the report. This cell represents the only user input required for this workbook.

## VIC
VIC | Regional data sheet
Utilisation summary data for report charting
Component | Category | 2000 | 2001 | 2002 | 2003 | 2004 | 2005 | 2006 | 2007 | 2008 | 2009 | 2010 | 2011
Actual data - linked to external set of utilisation spreadsheets (see discussion in S5.1)
Utilisation metric
Transformers | all | [6 empty] | 58.99% | 66.23% | 62.11% | 63.74% | 58.1% | 56.07%
| tie | 52.36% | [5 empty] | 55.83% | 66.97% | 57.31% | 57.76% | 52.32% | 53.29%
| terminal station | [6 empty] | 62.6% | 65.35% | 68.09% | 71.54% | 65.15% | 59.11% | 5.1.3 Table 4 data
Line | all | 23.98% | [5 empty] | 27.38% | 31.86% | 33.81% | 38.49% | 34.08% | 29.65% | average | proportion
| 500 | [6 empty] | 24.17% | 26.79% | 30.58% | 32.87% | 27.34% | 25.41% | 27.86% | 65.48%
| 330 | [6 empty] | 30.5% | 56.3% | 46.33% | 65.57% | 62.39% | 46.25% | 51.22% | 11.85%
| 275 | [13 empty] | 0%
| 220 | [6 empty] | 35.09% | 33.89% | 36.33% | 41.18% | 39.08% | 33.49% | 36.51% | 22.42%
| 132 | [13 empty] | 0%
| 110 | [13 empty] | 0%
| 66 | [6 empty] | 34.2% | 37.46% | 33.5% | 36.93% | 31.38% | 29.21% | 33.78% | 0.2588%
Loading (MVA) (sum of the MVA loading of each network element included in the utilisation metric)
Transformers | all | [6 empty] | 12901.2657 | 14437.8761 | 14297.089 | 15501.2277 | 14164.1136 | 14280.3551
| tie | [6 empty] | 6518.4419 | 7886.1245 | 7321.5571 | 7956.7803 | 7013.5173 | 7089.6216
| terminal station | [6 empty] | 6382.8238 | 6551.7516 | 6975.5319 | 7544.4474 | 7150.5962 | 7190.7335
Line | all | [6 empty] | 27084.7949 | 30318.2933 | 32309.7627 | 34136.097 | 31433.0582 | 29756.1774
| 500 | [6 empty] | 12601.4488 | 13935.4156 | 15365.0263 | 15888.4492 | 13377.1372 | 12915.1922
| 330 | [6 empty] | 1445.1669 | 2462.7974 | 2101.7095 | 2714.4529 | 2600.2774 | 1934.4456
| 275 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 220 | [6 empty] | 12626.3002 | 13459.7828 | 14395.512 | 15112.5841 | 15047.3756 | 14520.3502
| 132 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 110 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 66 | [6 empty] | 411.8789 | 460.2974 | 447.5148 | 420.6108 | 408.2681 | 386.1894
Capacity (MVA) (sum of the MVA rating (Rating A) of each network element included in the utilisation metric)
Transformers | all | [6 empty] | 21872 | 21801 | 23020 | 24321 | 24380 | 25470.5
| tie | [6 empty] | 11675 | 11775 | 12775 | 13775 | 13405 | 13305
| terminal station | [6 empty] | 10197 | 10026 | 10245 | 10546 | 10975 | 12165.5
Line | all | [6 empty] | 95698.056 | 95618.122 | 95629.932 | 91316.803 | 93978.233 | 96293.787
| 500 | [6 empty] | 48476.3 | 49078.3 | 47922.3 | 46621.9 | 47214.9 | 47922.3
| 330 | [6 empty] | 4902.637 | 4642.771 | 4811.247 | 4449.455 | 4539.092 | 4564.351
| 275 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 220 | [6 empty] | 41086.119 | 40664.051 | 41705.185 | 39054.248 | 40986.041 | 42568.936
| 132 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 110 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 66 | [6 empty] | 1233 | 1233 | 1191.2 | 1191.2 | 1238.2 | 1238.2
Length (km) (sum of the length (actual or estimate) of each line element included in the utilisation metric)
Line | all | [6 empty] | 5995.6148 | 6009.0588 | 6074.4556 | 6069.2123 | 6074.1401 | 6086.379
| 500 | [6 empty] | 1446.1047 | 1446.1047 | 1446.1047 | 1446.1047 | 1446.1047 | 1459.96
| 330 | [6 empty] | 724.0333 | 724.0333 | 724.0333 | 718.79 | 718.79 | 718.79
| 275 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 220 | [6 empty] | 3620.9881 | 3634.4321 | 3620.9881 | 3620.9881 | 3614.4574 | 3612.8409
| 132 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 110 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 66 | [6 empty] | 204.4888 | 204.4888 | 283.3296 | 283.3296 | 294.7881 | 294.7881
|  | MVA.length (MVA.km) (sum of the Capacity x Length of each line element included in the utilisation metric) | [11 empty] | average
Line | all | [6 empty] | 5631766.1139 | 5653223.3066 | 5664937.3729 | 5427377.6789 | 5515859.1231 | 5577013.7782 | 5578362.8956
| 500 | [6 empty] | 3678033.0915 | 3706216.1915 | 3670105.0315 | 3597127.8435 | 3605614.8335 | 3658428.911 | 3652587.6504
| 330 | [6 empty] | 708011.4284 | 659920.4986 | 687421.2614 | 628807.1815 | 637790.7076 | 643481.5603 | 660905.4396
| 275 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 220 | [6 empty] | 1232961.1063 | 1274326.1288 | 1292401.3965 | 1186432.9704 | 1256905.349 | 1259555.0738 | 1250430.3375
| 132 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 110 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 66 | [6 empty] | 12760.4878 | 12760.4878 | 15009.6836 | 15009.6836 | 15548.2331 | 15548.2331 | 14439.4681
Correctioned utilisation metrics (see discussion in sections 5.2, 5.2 and 6.1)
Corrected utilisation metric (S5.2 and S5.3)
Transformers | all | 0% | [5 empty] | 61.71% | 67.93% | 60.99% | 58.58% | 55.09% | 56.17%
| tie | 52.36% | [5 empty] | 58.41% | 68.7% | 56.28% | 53.09% | 49.61% | 53.38%
Line | all | 26.35% | [5 empty] | 33.26% | 35.97% | 37.8% | 36.92% | 34.44% | 33.56%
Corrected utilisation metric (S6.1)
Transformers | all | 0% | [5 empty] | 50.7% | 55.82% | 50.11% | 48.13% | 45.27% | 46.15%
| tie | 43.03% | [5 empty] | 47.99% | 56.45% | 46.24% | 43.62% | 40.77% | 43.86%
Line | all | 21.65% | [5 empty] | 27.33% | 29.55% | 31.06% | 30.34% | 28.3% | 27.57%
S5.2, S5.3 & S6 - calculations and supporting data
S5.2.1.1 - correction to account for weather on asset loading
| Year | 2000 | 2001 | 2002 | 2003 | 2004 | 2005 | 2006 | 2007 | 2008 | 2009 | 2010 | 2011
Actual demand | (MW) | 7832 | 8088 | 7621 | 8203 | 8574 | 8535 | 8730 | 9163.5296 | 9877.9998 | 10553.7197 | 10281.8414 | 9982.1393
Weather corrected | (MW) | 7832 | 8088 | 7983 | 8301 | 8602 | 8894 | 9133 | 9400 | 9700 | 9700 | 9750 | 10000
% adjust to weather correct | (5.2.1.1 Table 5) | 100% | 100% | 104.8% | 101.2% | 100.3% | 104.2% | 104.6% | 102.6% | 98.2% | 91.91% | 94.83% | 100.2%
utilisation metric (weather corrected MD)
Transformers | all | [6 empty] | 61.71% | 67.93% | 60.99% | 58.58% | 55.09% | 56.17%
| tie | 52.36% | [5 empty] | 58.41% | 68.7% | 56.28% | 53.09% | 49.61% | 53.38%
| TS | [6 empty] | 65.48% | 67.03% | 66.86% | 65.75% | 61.78% | 59.21%
Line | all | 23.98% | [5 empty] | 28.64% | 32.68% | 33.2% | 35.38% | 32.32% | 29.7%
S5.2.1.2 - Conversion to static ratings for comparison to NSW and QLD (assumes equivalent static rating would be 45C design temp for VIC)
| Year | 2000 | 2001 | 2002 | 2003 | 2004 | 2005 | 2006 | 2007 | 2008 | 2009 | 2010 | 2011
Temperature | (degrees C) | [6 empty] | 34.4 | 38.6 | 36 | 42.3 | 40.9 | 36.6
adjustments to line rating |  | 91% | [5 empty] | 86.12% | 90.87% | 87.84% | 95.81% | 93.84% | 88.51%
5.2.1.2 Table 6 | Correction to utilisation | [6 empty] | 116.1% | 110% | 113.8% | 104.4% | 106.6% | 113%
correct line utilisation metric (includes MD weather correction) |  | 26.35% | [5 empty] | 33.26% | 35.97% | 37.8% | 36.92% | 34.44% | 33.56%
S5.3 - 2000 estimate of utilisation metric
| 2000 MD as % of 2006 | 85.75%
| capacity added 2000-2005 | MVA | % change from 2006 capacity
(5.3.1 Table 7) | tie transformers | 1000 | 91.43%
| lines | 2000 | 97.91%
2000 utilisation metric (based on actuals)
| tie transformers | 52.36%
| lines | 23.98%
S6 - corrections summary
issue | correction | tx | line
diversity | 100% | 1 | 1
peakiness | 82.17% | 1 | 1
line ratings | 100% |  | 1
Total correction |  | 82.17% | 82.17%
peakiness correction (S6.1.2) |  |  |  | (estimated % reduction from SOO demand duration curves)
|  |  | SOO year | 1999 | 2005/06 | 2006/07 | 2007/08 | 2008/09 | 2009/10 | 2010/11 | average
|  |  | % reduction from maximum demand to demand only exceeded 1% of time | 13 | 13 | 12 | 17.5 | 22 | 21.5 | 21 | 17.8333
Density calculation (S6.2)
| year | 2000 | 2001 | 2002 | 2003 | 2004 | 2005 | 2006 | 2007 | 2008 | 2009 | 2010 | 2011
| MW MD | 0 | 8088 | 7618 | 8202 | 8572 | 8566 | 8788 | 9134 | 9878 | 10505 | 10188 | 9481
| km transmission line |  |  |  |  | 6553 | 6553 | 6553 | 6553 | 6553 | 6553
| density (MW/km) |  |  |  |  | 1.3081 | 1.3072 | 1.3411 | 1.3939 | 1.5074 | 1.6031
Density 5-year average (2004/05 - 2008/09) (MW/km) |  |  | 1.4305 | (used for charting)
Note on C4: The external set of spreadsheets contain the OPDMS data files and calcuations that are described in S5.1 of the report
Note on C7: Estimate for 2000 is calculated below
Note on C9: Estimate for 2000 is calculated below
Note on C59: The external set of spreadsheets contain the OPDMS data files and calcuations that are described in S5.1 of the report
Note on A72: 2002 SOO, 2006 and 2011 APR
Note on A73: 2006 and 2011 APR
Note on C73: No weather corrected data - so use actual
Note on A84: detailed calculations not included in this workbook
Note on C92: Cranbourne - 1000MVA
Note on C93: Latrobe Valley - 2000 MVA
Note on J108: Estimated as data not available
Note on B113: From AEMO data
Note on B114: From AER 2009/10 TNSP performance report

## NSW
NSW | Regional data sheet
Utilisation summary data for report charting
Component | Category | 2000 | 2001 | 2002 | 2003 | 2004 | 2005 | 2006 | 2007 | 2008 | 2009 | 2010 | 2011
Actual data - linked to external set of utilisation spreadsheets (see discussion in S5.1)
Utilisation metric
Transformers | all | [6 empty] | 47.98% | 48.74% | 50.9% | 44.4% | 41.89% | 39.71%
| tie | 48.41% | [5 empty] | 48.23% | 49.4% | 51.71% | 45.1% | 43.38% | 44.38%
| terminal station | [6 empty] | 36.76% | 35.22% | 36.6% | 31.88% | 22.22% | 8.897% | 5.1.3 Table 4 data
Line | all | 34.46% | [5 empty] | 37.54% | 32.2% | 34.84% | 34.13% | 28.4% | 32.31% | average | proportion
| 500 | [6 empty] | 20.69% | 20.91% | 26.85% | 20.55% | 8.296% | 9.211% | 17.75% | 18.02%
| 330 | [6 empty] | 40.44% | 34.38% | 36.66% | 35.39% | 39.2% | 45.84% | 38.65% | 71.16%
| 275 | [13 empty] | 0%
| 220 | [6 empty] | 21.76% | 17.51% | 18.27% | 58.43% | 28.67% | 35.72% | 30.06% | 1.802%
| 132 | [6 empty] | 33.73% | 26.21% | 29.3% | 31.61% | 31.76% | 30.22% | 30.47% | 8.89%
| 110 | [13 empty] | 0%
| 66 | [7 empty] | 30.91% | 41.08% | 21.55% | 10.82% | 19.03% |  | 0.129%
Loading (MVA) (sum of the MVA loading of each network element included in the utilisation metric)
Transformers | all | [6 empty] | 10936.0171 | 11566.1554 | 12080.8093 | 10872.361 | 11267.9897 | 11933.7024
| tie | [6 empty] | 10752.1941 | 11178.7256 | 11612.3245 | 10464.2973 | 10846.855 | 11582.0033
| terminal station | [6 empty] | 183.823 | 387.4298 | 468.4848 | 408.0637 | 421.1347 | 351.6991
Line | all | [6 empty] | 37296.1685 | 35250.4156 | 40017.3711 | 38026.9147 | 42212.5338 | 47554.0444
| 500 | [6 empty] | 856.7011 | 865.6424 | 1111.6662 | 850.6052 | 1637.2739 | 1674.7068
| 330 | [6 empty] | 25435.5264 | 24459.5967 | 27650.8002 | 23168.0349 | 26228.2297 | 29552.872
| 275 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 220 | [6 empty] | 122.957 | 96.7654 | 106.2417 | 368.1529 | 174.315 | 222.6256
| 132 | [6 empty] | 10880.984 | 9652.508 | 10932.8093 | 13445.6409 | 13960.141 | 15906.2225
| 110 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 66 | [6 empty] | 0 | 175.9031 | 215.8536 | 194.4807 | 212.5741 | 197.6174
Capacity (MVA) (sum of the MVA rating (Rating A) of each network element included in the utilisation metric)
Transformers | all | [6 empty] | 22795 | 23730 | 23735 | 24485 | 26900 | 30052
| tie | [6 empty] | 22295 | 22630 | 22455 | 23205 | 25005 | 26099
| terminal station | [6 empty] | 500 | 1100 | 1280 | 1280 | 1895 | 3953
Line | all | [6 empty] | 99783 | 116072 | 119411 | 115009 | 137874 | 145296
| 500 | [6 empty] | 4140 | 4140 | 4140 | 4140 | 17514 | 18407
| 330 | [6 empty] | 65479 | 75362 | 78035 | 69457 | 75629 | 74601
| 275 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 220 | [6 empty] | 623 | 623 | 623 | 623 | 623 | 623
| 132 | [6 empty] | 29541 | 35439 | 36105 | 40223 | 42561 | 50945
| 110 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 66 | [6 empty] | 0 | 508 | 508 | 566 | 1547 | 720
Length (km) (sum of the length (actual or estimate) of each line element included in the utilisation metric)
Line | all | [6 empty] | 10590.2911 | 11115.4881 | 11273.321 | 11390.6438 | 12849.633 | 12258.3314
| 500 | [6 empty] | 286.6 | 286.6 | 286.6 | 286.6 | 1277.0447 | 1018
| 330 | [6 empty] | 5080.2609 | 5254.5609 | 5297.8392 | 5227.8237 | 5359.2452 | 4806.2
| 275 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 220 | [6 empty] | 657.3 | 657.3 | 657.3 | 657.3 | 657.3 | 657.3
| 132 | [6 empty] | 4566.1302 | 4811.5977 | 4926.1523 | 5056.0608 | 5392.2798 | 5587.1928
| 110 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 66 | [6 empty] | 0 | 105.4295 | 105.4295 | 162.8594 | 163.7633 | 189.6386
|  | MVA.length (MVA.km) (sum of the Capacity x Length of each line element included in the utilisation metric) | [11 empty] | average
Line | all | [6 empty] | 6126977.8011 | 7107044.321 | 7216442.1886 | 6581185.1704 | 9087107.6743 | 8322107.8692 | 7406810.8374
| 500 | [6 empty] | 593262 | 593262 | 593262 | 593262 | 2945065.2593 | 2689871.2 | 1334664.0765
| 330 | [6 empty] | 4875992.8296 | 5730111.8224 | 5820196.7963 | 5209935.5687 | 5295029.0902 | 4692780.8 | 5270674.4845
| 275 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 220 | [6 empty] | 133438.3 | 133438.3 | 133438.3 | 133438.3 | 133438.3 | 133438.3 | 133438.3
| 132 | [6 empty] | 524284.6716 | 644109.6659 | 663422.5596 | 634250.6031 | 690929.0715 | 793868.8375 | 658477.5682
| 110 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 66 | [6 empty] | 0 | 6122.5327 | 6122.5327 | 10298.6985 | 22645.9533 | 12148.7317 | 9556.4081
Correctioned utilisation metrics (see discussion in sections 5.2, 5.2 and 6.1)
Corrected utilisation metric (S5.2 and S5.3)
Transformers | all | 0% | [5 empty] | 48.46% | 46.35% | 48.43% | 43.51% | 41.72% | 37.78%
| tie | 48.41% | [5 empty] | 48.72% | 46.98% | 49.21% | 44.19% | 43.2% | 42.22%
Line | all | 34.46% | [5 empty] | 37.93% | 30.62% | 33.15% | 33.44% | 28.28% | 30.74%
Corrected utilisation metric (S6.1)
Transformers | all | 0% | [5 empty] | 42.49% | 40.64% | 42.46% | 38.15% | 36.57% | 33.12%
| tie | 42.44% | [5 empty] | 42.71% | 41.18% | 43.14% | 38.74% | 37.87% | 37.01%
Line | all | 30.21% | [5 empty] | 33.25% | 26.84% | 29.06% | 29.32% | 24.79% | 26.95%
S5.2, S5.3 & S6 - calculations and supporting data
S5.2.1.1 - correction to account for weather on asset loading | [7 empty] | winter peaking to 2008 (inc) |  |  | change to summer peaking
| Year | 2000 | 2001 | 2002 | 2003 | 2004 | 2005 | 2006 | 2007 | 2008 | 2009 | 2010 | 2011
Actual demand | (MW) | 12062.6318 | 11927 | 12321 | 12641 | 13107 | 13198 | 13166 | 13985 | 14398 | 14287 | 13957 | 14820
Weather corrected | (MW) | 12062.6318 | 11927 | 12600 | 12700 | 12900 | 13100 | 13300 | 13300 | 13700 | 14000 | 13900 | 14100
% adjust to weather correct | (5.2.1.1 Table 5) | 100% | 100% | 102.3% | 100.5% | 98.42% | 99.26% | 101% | 95.1% | 95.15% | 97.99% | 99.59% | 95.14%
utilisation metric (weather corrected MD)
Transformers | all | [6 empty] | 48.46% | 46.35% | 48.43% | 43.51% | 41.72% | 37.78%
| tie | 48.41% | [5 empty] | 48.72% | 46.98% | 49.21% | 44.19% | 43.2% | 42.22%
| TS | [6 empty] | 37.14% | 33.5% | 34.83% | 31.24% | 22.13% | 8.465%
Line | all | 34.46% | [5 empty] | 37.93% | 30.62% | 33.15% | 33.44% | 28.28% | 30.74%
S5.2.1.2 - Conversion to static ratings - not relevant to NSW calcuations
S5.3 - 2000 estimate of utilisation metric
| 2000 MD as % of 2006 | 90.7%
| capacity added 2000-2005 | MVA | % change from 2006 capacity
(5.3.1 Table 7) | tie transformer | 2150 | 90.36%
| lines | 1175 | 98.82%
2000 utilisation metric (based on actuals)
| tie transformers | 48.41%
| lines | 34.46%
S6 - corrections summary
issue | correction | tx | line
diversity | 100% | 1 | 1
peakiness | 87.67% | 1 | 1
line ratings | 100% |  | 1
Total correction |  | 87.67% | 87.67%
peakiness correction (S6.1.2) |  |  |  | (estimated % reduction from SOO demand duration curves)
|  |  | SOO year | 1999 | 2005/06 | 2006/07 | 2007/08 | 2008/09 | 2009/10 | 2010/11 | average
|  |  | % reduction from maximum demand to demand only exceeded 1% of time | 11 | 9 | 10 | 13 | 12 | 14 | 16 | 12.3333
Density calculation (S6.2)
| year | 2000 | 2001 | 2002 | 2003 | 2004 | 2005 | 2006 | 2007 | 2008 | 2009 | 2010 | 2011
| MW MD | 0 | 11572 | 10990 | 12456 | 12216 | 12946 | 13462 | 12981 | 13071 | 14288 | 14051 | 13767
| km transmission line |  |  |  |  | 13109 | 13148 | 13301 | 13310 | 13327 | 13330
| density (MW/km) |  |  |  |  | 0.93188 | 0.98464 | 1.0121 | 0.97528 | 0.98079 | 1.0719
Density 5-year average (2004/05 - 2008/09) (MW/km) |  |  | 1.005 | (used for charting)
Note on C4: The external set of spreadsheets contain the OPDMS data files and calcuations that are described in S5.1 of the report
Note on C7: Estimate for 2000 is calculated below
Note on C9: Estimate for 2000 is calculated below
Note on C59: The external set of spreadsheets contain the OPDMS data files and calcuations that are described in S5.1 of the report
Note on A72: 2007 and 2011 APR
Note on A73: 2011 APR
Note on C73: No weather corrected data - so use actual
Note on B92: Waratah West - 375 MVA Tuggerah - 375 MVA Balranald - 50 MVA Canberra - 400 MVA Regentville - 375 MVA Tamworth - 200 MVA Vinyard - 375 MVA
Note on B93: 330 kV cable to Haymarket - 750 MVA Coff Harbour – Kempsey 132 kV line - 153, 122 MVA Armidale-Kempsey 132 kV line - 30 MVA Armidale-Koolkhan 132 kV line - 30 MVA Molong-Malindra 132 kV line - 100 MVA
Note on J108: Estimated as data not available
Note on B113: From AEMO data
Note on B114: From AER 2009/10 TNSP performance report (includes TransGrid and Ausgrid transmission lines)

## QLD
QLD | Regional data sheet
Utilisation summary data for report charting
Component | Category | 2000 | 2001 | 2002 | 2003 | 2004 | 2005 | 2006 | 2007 | 2008 | 2009 | 2010 | 2011
Actual data - linked to external set of utilisation spreadsheets (see discussion in S5.1)
Utilisation metric
Transformers | all | [6 empty] | 44.83% | 42.95% | 37.63% | 37.37% | 36.3% | 37.1%
| tie | 49.85% | [5 empty] | 45.14% | 43.16% | 38.59% | 38.18% | 36.81% | 38.14%
| terminal station | [6 empty] | 43.8% | 42.24% | 34.17% | 34.47% | 34.48% | 33.02% | 5.1.3 Table 4 data
Line | all | 30.6% | [5 empty] | 36.58% | 35.5% | 28.08% | 28.25% | 28.56% | 27.15% | average | proportion
| 500 | [13 empty] | 0%
| 330 | [6 empty] | 13.78% | 19.52% | 23.06% | 32.44% | 31.98% | 40.74% | 26.92% | 7.746%
| 275 | [6 empty] | 38.93% | 37.68% | 28.72% | 28.13% | 28.18% | 26.32% | 31.33% | 80.13%
| 220 | [13 empty] | 0%
| 132 | [6 empty] | 34.63% | 31.53% | 26.56% | 25.59% | 28.23% | 22.72% | 28.21% | 10.23%
| 110 | [6 empty] | 39.89% | 28.23% | 30.85% | 30.28% | 32.12% | 30.51% | 31.98% | 1.897%
| 66 | [13 empty] | 0%
Loading (MVA) (sum of the MVA loading of each network element included in the utilisation metric)
Transformers | all | [6 empty] | 8736.7001 | 9078.3778 | 9379.2509 | 9603.8546 | 9327.5929 | 10217.7587
| tie | [6 empty] | 6798.5165 | 7003.125 | 7528.4185 | 7665.0356 | 7388.711 | 8360.8909
| terminal station | [6 empty] | 1938.1836 | 2075.2527 | 1850.8324 | 1938.819 | 1938.8819 | 1856.8679
Line | all | [6 empty] | 29911.0126 | 31847.8632 | 29795.2288 | 31531.0589 | 32292.2338 | 32561.0014
| 500 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 330 | [6 empty] | 1382.2523 | 1848.7073 | 2479.2929 | 3024.0688 | 2829.6998 | 3364.2044
| 275 | [6 empty] | 19038.2219 | 21008.5615 | 19202.306 | 19770.8582 | 19707.4112 | 19398.3913
| 220 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 132 | [6 empty] | 5106.05 | 5091.7177 | 4519.5872 | 4809.1557 | 5377.0568 | 4714.7582
| 110 | [6 empty] | 4384.4884 | 3898.8768 | 3594.0427 | 3926.9762 | 4378.0659 | 5083.6475
| 66 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
Capacity (MVA) (sum of the MVA rating (Rating A) of each network element included in the utilisation metric)
Transformers | all | [6 empty] | 19487 | 21138 | 24923 | 25698 | 25698 | 27543
| tie | [6 empty] | 15062 | 16225 | 19507 | 20074 | 20074 | 21919
| terminal station | [6 empty] | 4425 | 4913 | 5416 | 5624 | 5624 | 5624
Line | all | [6 empty] | 82253 | 91472.3 | 104480 | 112962 | 109307 | 116366.347
| 500 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 330 | [6 empty] | 8226 | 8226 | 9472 | 9472 | 9472 | 9472
| 275 | [6 empty] | 48618 | 56476 | 65662 | 70158 | 66576 | 69057.114
| 220 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 132 | [6 empty] | 14710 | 15103.3 | 16769 | 19862 | 19773 | 21139.233
| 110 | [6 empty] | 10699 | 11667 | 12577 | 13470 | 13486 | 16698
| 66 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
Length (km) (sum of the length (actual or estimate) of each line element included in the utilisation metric)
Line | all | [6 empty] | 13142.4187 | 13003.6887 | 13608.4626 | 14073.6081 | 13653.3914 | 13842.2313
| 500 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 330 | [6 empty] | 320.6595 | 320.6595 | 413.637 | 413.637 | 413.637 | 413.637
| 275 | [6 empty] | 6081.5624 | 6291.0407 | 6817.4438 | 6989.1237 | 6608.5595 | 6765.06
| 220 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 132 | [6 empty] | 5781.324 | 5543.0961 | 5609.3662 | 5870.8618 | 5831.2093 | 5695.3333
| 110 | [6 empty] | 958.8728 | 848.8925 | 768.0155 | 799.9856 | 799.9856 | 968.201
| 66 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
|  | MVA.length (MVA.km) (sum of the Capacity x Length of each line element included in the utilisation metric) | [11 empty] | average
Line | all | [6 empty] | 4925026.8691 | 5053929.2276 | 5915893.2865 | 6285138.423 | 6045711.0377 | 6426353.1649 | 5775342.0014
| 500 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 330 | [6 empty] | 370122.0166 | 370122.0166 | 485972.0717 | 485972.0717 | 485972.0717 | 485972.0717 | 447355.3867
| 275 | [6 empty] | 3876694.3323 | 4037440.0835 | 4760870.2932 | 5068743.4163 | 4836220.6486 | 5186715.9925 | 4627780.7944
| 220 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 132 | [6 empty] | 558973.4246 | 542888.3581 | 572244.3882 | 627764.6394 | 620162.4218 | 621954.122 | 590664.559
| 110 | [6 empty] | 119237.0955 | 103478.7693 | 96806.5334 | 102658.2956 | 103355.8956 | 131710.9786 | 109541.2614
| 66 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
Correctioned utilisation metrics (see discussion in sections 5.2, 5.2 and 6.1)
Corrected utilisation metric (S5.2 and S5.3)
Transformers | all | 0% | [5 empty] | 44.83% | 42.95% | 37.63% | 37.37% | 36.3% | 37.1%
| tie | 49.85% | [5 empty] | 45.14% | 43.16% | 38.59% | 38.18% | 36.81% | 38.14%
Line | all | 30.6% | [5 empty] | 36.58% | 35.5% | 28.08% | 28.25% | 28.56% | 27.15%
Corrected utilisation metric (S6.1)
Transformers | all | 0% | [5 empty] | 44.06% | 42.21% | 36.98% | 36.73% | 35.67% | 36.46%
| tie | 48.99% | [5 empty] | 44.36% | 42.42% | 37.93% | 37.52% | 36.17% | 37.48%
Line | all | 26.15% | [5 empty] | 31.25% | 30.33% | 23.99% | 24.14% | 24.4% | 23.2%
S5.2, S5.3 & S6 - calculations and supporting data
S5.2.1.1 - correction to account for weather on asset loading
| Year | 2000 | 2001 | 2002 | 2003 | 2004 | 2005 | 2006 | 2007 | 2008 | 2009 | 2010 | 2011
Actual demand | (MW) | 5620 | 5830 | 6183 | 6336 | 7020 | 7282 | 7373 | 7889 | 7464 | 8021 | 8293 | 8109
Weather corrected | (MW) | 5544 | 5883 | 6135 | 6368 | 6818 | 7298 | 7649 | 7950 | 8032 | 8439 | 8621 | 8700
% adjust to weather correct | (5.2.1.1 Table 5) | 98.65% | 100.9% | 99.22% | 100.5% | 97.12% | 100.2% | 103.7% | 100.8% | 107.6% | 105.2% | 104% | 107.3%
utilisation metric (weather corrected MD) - not used as anomaly in weather corrected data
Transformers | all | [6 empty] | 46.51% | 43.28% | 40.5% | 39.32% | 37.73% | 39.8%
| tie | 49.18% | [5 empty] | 46.83% | 43.5% | 41.53% | 40.17% | 38.26% | 40.92%
| TS | [6 empty] | 45.44% | 42.57% | 36.77% | 36.27% | 35.84% | 35.42%
Line | all | 30.19% | [5 empty] | 37.94% | 35.77% | 30.22% | 29.72% | 29.69% | 29.13%
S5.2.1.2 - Conversion to static ratings - not relevant to QLD calcuations
S5.3 - 2000 estimate of utilisation metric
| 2000 MD as % of 2006 | 76.22% | (for QLD using actual as weather correction to 50% PoE appears anomalous)
| capacity added 2000-2005 | MVA | % change from 2006 capacity
(5.3.1 Table 7) | tie transformers | 4667 | 69.01%
| lines | 7315 | 91.11%
2000 utilisation metric (based on actuals)
| tie transformers | 49.85%
| lines | 30.6%
S6 - corrections summary
issue | correction | tx | line
diversity | 107.4% | 1 | 1 |  | S6.1.1 QLD adjustments for load diversity |  |  |  | 7.4%
peakiness | 91.5% | 1 | 1 |  | S6.1.3 - Possible adjustment to allow for existing conservative static rating
line ratings | 86.96% |  | 1 |  | (noting that it appears that a boost of 40% at peak demand could be achieved)
Total correction |  | 98.27% | 85.45% |  | Adjustment | 15% | increase in capacity to put on same basis as VIC and NSW
peakiness correction (S6.1.2) |  |  |  | (estimated % reduction from SOO demand duration curves)
|  |  | SOO year | 1999 | 2005/06 | 2006/07 | 2007/08 | 2008/09 | 2009/10 | 2010/11 | average
|  |  | % reduction from maximum demand to demand only exceeded 1% of time | 4 | 4 | 10 | 7 | 8 | 10 | 12 | 8.5
Density calculation (S6.2)
| year | 2000 | 2001 | 2002 | 2003 | 2004 | 2005 | 2006 | 2007 | 2008 | 2009 | 2010 | 2011
| MW MD | 0 | 6580 | 7002 | 7082 | 7912 | 8176 | 8280 | 8673 | 8177 | 8812 | 9070 | 9702
| km transmission line |  |  |  |  | 11516 | 11902 | 11939 | 12132 | 12671 | 13106
| density (MW/km) |  |  |  |  | 0.68704 | 0.68694 | 0.69353 | 0.71489 | 0.64533 | 0.67236
Density 5-year average (2004/05 - 2008/09) (MW/km) |  |  | 0.68207 | (used for charting)
Note on C4: The external set of spreadsheets contain the OPDMS data files and calcuations that are described in S5.1 of the report
Note on C7: Estimate for 2000 is calculated below
Note on C9: Estimate for 2000 is calculated below
Note on C59: The external set of spreadsheets contain the OPDMS data files and calcuations that are described in S5.1 of the report
Note on A72: 2006 and 2011 APR
Note on N72: Using correction for flood and cyclone as discussed in APR
Note on A73: 2006 and 2011 APR
Note on C92: Middle Ridge - 250 MVA Woree - 410 MVA Loganlea - 2 x 440 MVA Molendinar - 300 MVA Strathmore - 410 MVA Edmonton - 300 MVA Nebo - 275 MVA Rocklea - 440 MVA Loganlea, Woolooga, Palmwoods, Swanbank - 440, 275, 412, 275 MVA
Note on C93: Belmont 275 kV - 2 x 655 MVA Millmerran – Middle Ridge 275 kV - 2 x 1246 MVA Chalumbin-Springmount 275 kV - 2 x 460 MVA Stanwell-Broadsound 275 kV - 880 + 663 MVA Broadsound-Lilyvale 275 kV - 550 MVA Maudsland-Molendinar 275 kV - 500 MVA
Note on F101: Note: this adjustment has been calcuated on separate worksheets, based upon a set of OPDMS data files.
Note on J108: Estimated as data not available
Note on B113: From AEMO data
Note on B114: From AER 2009/10 TNSP performance report

## Utilisation charting
Charting data (linked to regional data sheets)
|  | 2000 | 2001 | 2002 | 2003 | 2004 | 2005 | 2006 | 2007 | 2008 | 2009 | 2010 | 2011 | [6 empty] | row pointer 1 | row pointer 2
Actual utilisation metric
Transformers
all | VIC | 2006: 58.99%; 2007: 66.23%; 2008: 62.11%; 2009: 63.74%; 2010: 58.1%; 2011: 56.07% | [7 empty] | 6
| NSW | 2006: 47.98%; 2007: 48.74%; 2008: 50.9%; 2009: 44.4%; 2010: 41.89%; 2011: 39.71% | [7 empty] | 6
| QLD | 2006: 44.83%; 2007: 42.95%; 2008: 37.63%; 2009: 37.37%; 2010: 36.3%; 2011: 37.1% | [7 empty] | 6
tie | VIC | 2000: 52.36%; 2006: 55.83%; 2007: 66.97%; 2008: 57.31%; 2009: 57.76%; 2010: 52.32%; 2011: 53.29% | [7 empty] | 7
| NSW | 2000: 48.41%; 2006: 48.23%; 2007: 49.4%; 2008: 51.71%; 2009: 45.1%; 2010: 43.38%; 2011: 44.38% | [7 empty] | 7
| QLD | 2000: 49.85%; 2006: 45.14%; 2007: 43.16%; 2008: 38.59%; 2009: 38.18%; 2010: 36.81%; 2011: 38.14% | [7 empty] | 7
TS | VIC | 2006: 62.6%; 2007: 65.35%; 2008: 68.09%; 2009: 71.54%; 2010: 65.15%; 2011: 59.11% | [7 empty] | 8
| NSW | 2006: 36.76%; 2007: 35.22%; 2008: 36.6%; 2009: 31.88%; 2010: 22.22%; 2011: 8.897% | [7 empty] | 8
| QLD | 2006: 43.8%; 2007: 42.24%; 2008: 34.17%; 2009: 34.47%; 2010: 34.48%; 2011: 33.02% | [7 empty] | 8
Lines
all | VIC | 2000: 23.98%; 2006: 27.38%; 2007: 31.86%; 2008: 33.81%; 2009: 38.49%; 2010: 34.08%; 2011: 29.65% | [7 empty] | 9
| NSW | 2000: 34.46%; 2006: 37.54%; 2007: 32.2%; 2008: 34.84%; 2009: 34.13%; 2010: 28.4%; 2011: 32.31% | [7 empty] | 9
| QLD | 2000: 30.6%; 2006: 36.58%; 2007: 35.5%; 2008: 28.08%; 2009: 28.25%; 2010: 28.56%; 2011: 27.15% | [7 empty] | 9
Corrected utilisation metric (S5 and S6 corrections) | [13 empty] | S6 - utilisation vs density analysis | [5 empty] | d117
(not included S6 corrections) | [16 empty] | average utilisation |  |  | yes
Transformer | [13 empty] | Density (MW/km) |  |  | (2006-2007) | (2006-2011) | (2010-2011) | S5+S6 pointer | S5 pointer
tie | VIC | 2000: 52.36%; 2006: 58.41%; 2007: 68.7%; 2008: 56.28%; 2009: 53.09%; 2010: 49.61%; 2011: 53.38% | 1.4305 | 1.4305 | 1.4305 | 63.56% | 56.58% | 51.5% | 66 | 62
| NSW | 2000: 48.41%; 2006: 48.72%; 2007: 46.98%; 2008: 49.21%; 2009: 44.19%; 2010: 43.2%; 2011: 42.22% | 1.005 | 1.005 | 1.005 | 47.85% | 45.75% | 42.71% | 66 | 62
| QLD | 2000: 49.85%; 2006: 45.14%; 2007: 43.16%; 2008: 38.59%; 2009: 38.18%; 2010: 36.81%; 2011: 38.14% | 0.68207 | 0.68207 | 0.68207 | 44.15% | 40% | 37.48% | 66 | 62
Line
all | VIC | 2000: 26.35%; 2006: 33.26%; 2007: 35.97%; 2008: 37.8%; 2009: 36.92%; 2010: 34.44%; 2011: 33.56% | 1.4305 | 1.4305 | 1.4305 | 34.61% | 35.32% | 34% | 67 | 63
| NSW | 2000: 34.46%; 2006: 37.93%; 2007: 30.62%; 2008: 33.15%; 2009: 33.44%; 2010: 28.28%; 2011: 30.74% | 1.005 | 1.005 | 1.005 | 34.27% | 32.36% | 29.51% | 67 | 63
| QLD | 2000: 30.6%; 2006: 36.58%; 2007: 35.5%; 2008: 28.08%; 2009: 28.25%; 2010: 28.56%; 2011: 27.15% | 0.68207 | 0.68207 | 0.68207 | 36.04% | 30.68% | 27.85% | 67 | 63
Charts
Annual trend in utilisation
Transformer - all
5.1.2 - Fig 2 - WA actual - all transformers | [13 empty] | 5.1.2 - Fig 3 - WA actual - tie and TS transformers
5.3.2/6.1.4 - Fig 7/Fig 9 - tie transformers (2000 estimate) |  | 2005: (not included S6 corrections) | 5.2.2 - Fig 5 - WA actual vs corrected - tie transformers
Lines - all
5.1.3 - Fig 4 - WA actual - all lines | [13 empty] | 5.2.2 - Fig 6 - WA actual vs corrected - lines
5.3.3/6.1.4 - Fig 8/Fig 10 - lines (2000 estimate) |  | 2005: (not included S6 corrections)
[14 empty] | Do not include S6 corrections in charts (yes/no)? |  |  |  | yes | (Use to toggle between including Section 6 corrections or only those in Section 5)
Average utilisation vs density metric
| Equivalent to Fig 11 - tie transformers | 2006: 6.1.4 - Fig 11 - lines average utilisation vs density | (not included S6 corrections)
(must not include S6 corrections for report)
Note on U2: This shaded area includes pointers and switches to determine what data should be charted
Note on U22: Pointer to cell reference in regional data sheets. Required to reference the density measure.
Note on U23: linked to input in S98 below Switch for including Section 6 corrections or only those in Section 5
Note on H55: Use S98 to change plot to include Section 6 corrections
Note on H94: Use S98 to change plot to include Section 6 corrections
Note on O114: Use S98 to change plot to include Section 6 corrections