## Substations
Notes:
Substations with a Primary Voltage >=110KV only
Transformers ratings should be nominal nameplate at highest continuous rating - i.e with pumps / fans on where applicable
Substation | Voltage Ratio | Number of Transformers | Transformer Ratings | "N" Rating | "N-1" Rating | Summer Peak Load | Classification |  |  |  | Comments
|  |  | MVA | MVA | MVA | MVA
Substation 1 | 220/110 | 1 | 200 | 200 | see comment | 67.8 | Shared | 33.9% |  | Summer | 110kV bus is supplied via the parallel 110kV network, so N-1 rating is not zero.
Substation 2 | 220/110 | 4 | 260/260/260/200 | 980 | 720 | 309.8 | Shared | 31.61% | 1 | 19.56% | Reduced from previous year due to new 220kV injection point in Hobart (Lindisfarne) commissioned in 2011, and installation of various 110kV capacitors. Winter 2010 maximum was 512MVA.
Substation 3 | 220/110 | 2 | 150 | 300 | 150 | 75.7 | Shared | 25.23% | 2 | 25.23%
Substation 4 | 220/110 | 3 | 260/200/200 | 660 | 400 | 129.1 | Shared | 19.56% | 3 | 28.23% | Measured on 110kV side (others measured on 220kV side). Annual peak is on 13/5/2011: 142.4MVA
Substation 5 | 220/110 | 2 | 200 | 400 | 200 | 112.9 | Shared | 28.23% | 4 | 31.61% | 110kV bus is supplied via both these transformeres and the parallel 110kV network, so N-1 rating is not truly 200MVA.
Substation 6 | 220/110 | 2 | 200 | 400 | 200 | 181.7 | Shared | 45.42% | 5 | 33.9% | 110kV bus is supplied via both these transformeres and the parallel 110kV network, so N-1 rating is not truly 200MVA.
Substation 7 | 220/110 | 1 | 200 | 200 | 0 | 70.4 | Shared | 35.2% | 6 | 35.2% | 110kV bus is supplied via the parallel 110kV network, so N-1 rating is not zero.
Substation 8 | 220/110 | 2 | 150 | 300 | 150 | 112.8 | Shared | 37.6% | 7 | 37.6% | 110kV bus is supplied via both these transformeres and the parallel 110kV network, so N-1 rating is not truly 150MVA.
Substation 9 | 110/44 | 2 | 30 | 60 | 30 | 26.2 | Shared | 43.67% | 8 | 43.67%
[9 empty] | 9 | 45.42%
|  |  |  | 388.8889 |  |  |  |  | Mean | 33.38%
Connection
Connection
Note on G5: Unless stated otherwise in Comments, summer and winter load data for transformers which supply customer loads are from metering data; data for 220:110kV and 110:44kV transformers extracted from SCADA system.
Note on H5: Shared = shared nework asset "Connection" = DNSP connection assets "Connection MI" = assets to connect direct contracted major industrial customer "Connection - Dual" = assets to connect both DNSP and industrial customer.

## Lines
Notes:
Lines >=110KV only
Ratings ratings should be nominal based on "nominal" wind / temperature design
Line | Voltage | Nominal Rating | Non Thermal Rating Constraints | Summer Peak Load | Classification | NCSPS? 1=yes | Comments |  |  | 0%
|  | Summer (MVA) | Yes / No | MVA | [5 empty] | 0%
Transmission Circuit 1 | 110 | 64.9692 |  | 10.5748 | shared |  |  | 16.28% |  | 0%
Transmission Circuit 2 | 110 | 104.408 |  | 31.4942 | shared |  |  | 30.16% |  | 0%
Transmission Circuit 3 | 110 | 55.0619 |  | 30.8102 | shared |  |  | 55.96% |  | 0%
Transmission Circuit 4 | 110 | 64.9692 |  | 58.3709 | shared |  |  | 89.84% |  | 0%
Transmission Circuit 5 | 110 | 57.1577 |  | 57.8032 | shared |  |  | 101.1% |  | 0%
Transmission Circuit 6 | 110 | 153.9447 |  | 73.4346 | shared |  |  | 47.7% |  | 0%
Transmission Circuit 7 | 110 | 107.8375 |  | 14.8634 | shared |  |  | 13.78% |  | 0%
Transmission Circuit 8 | 110 | 107.8375 |  | 14.9484 | shared |  |  | 13.86% |  | 0%
Transmission Circuit 9 | 110 | 140.9889 |  | 50.3598 | shared |  |  | 35.72% |  | 0%
Transmission Circuit 10 | 110 | 140.9889 |  | 48.9341 | shared |  |  | 34.71% |  | 0%
Transmission Circuit 11 | 110 | 152.4205 |  | 44.65 | shared |  |  | 29.29% |  | 0%
Transmission Circuit 12 | 110 | 230.536 |  | 66.5903 | shared |  |  | 28.89%
Transmission Circuit 13 | 110 | 220.2476 |  | 91.6962 | shared |  |  | 41.63% |  | Summer
Transmission Circuit 14 | 110 | 104.408 |  | 44.5669 | shared |  |  | 42.69% | 1 | 0.818%
Transmission Circuit 15 | 110 | 61.7303 |  | 30.3273 | shared |  |  | 49.13% | 2 | 6.913%
Transmission Circuit 16 | 110 | 104.4 |  | 16.2896 | shared |  |  | 15.6% | 3 | 7.058%
Transmission Circuit 17 | 110 | 104.408 |  | 43.9013 | shared |  |  | 42.05% | 4 | 8.472%
Transmission Circuit 18 | 110 | 104.4 |  | 17.2489 | shared |  |  | 16.52% | 5 | 10.09%
Transmission Circuit 19 | 110 | 104.408 |  | 26.5453 | shared |  |  | 25.42% | 6 | 10.52%
Transmission Circuit 20 | 110 | 220.2476 |  | 82.6087 | shared |  |  | 37.51% | 7 | 12.92%
Transmission Circuit 21 | 110 | 89.3565 |  | 38.4946 | shared |  |  | 43.08% | 8 | 13.78%
Transmission Circuit 22 | 110 | 96.9775 |  | 48.582 | shared |  |  | 50.1% | 9 | 13.86%
Transmission Circuit 23 | 110 | 55.0619 |  |  | shared |  | Normally open | 0% | 10 | 14.14%
Transmission Circuit 24 | 110 | 96.9775 |  |  | shared |  | No 110kV VT at substation | 0% | 11 | 14.16%
Transmission Circuit 25 | 110 | 122.508 |  |  | shared |  | No 110kV VT at substation | 0% | 12 | 14.91%
Transmission Circuit 26 | 110 | 55.0619 |  |  | shared |  | No 110kV VT at substation | 0% | 13 | 15.09%
Transmission Circuit 27 | 110 | 104.408 |  | 27.2932 | shared |  |  | 26.14% | 14 | 15.6%
Transmission Circuit 28 | 110 | 104.408 |  | 21.431 | shared |  |  | 20.53% | 15 | 16.05%
Transmission Circuit 29 | 110 | 65.9219 |  | 22.4556 | shared |  |  | 34.06% | 16 | 16.28%
Transmission Circuit 30 | 110 | 104.408 |  |  | shared |  | Normally open | 0% | 17 | 16.52%
Transmission Circuit 31 | 220 | 332.2766 |  | 192.5493 | shared | 1 |  | 57.95% | 18 | 17.3%
Transmission Circuit 32 | 220 | 332.2766 |  | 193.2958 | shared | 1 |  | 58.17% | 19 | 18.01%
Transmission Circuit 33 | 220 | 334.1819 |  | 208.7259 | shared | 1 |  | 62.46% | 20 | 19.19%
Transmission Circuit 34 | 220 | 334.1819 |  | 207.6557 | shared | 1 |  | 62.14% | 21 | 19.9%
Transmission Circuit 35 | 110 | 153.9447 |  | 37.2974 | shared |  |  | 24.23% | 22 | 20.53%
Transmission Circuit 36 | 110 | 153.9447 |  | 13.042 | shared |  |  | 8.472% | 23 | 21.58%
Transmission Circuit 37 | 110 | 111.2669 |  | 35.5462 | shared |  |  | 31.95% | 24 | 23.15%
Transmission Circuit 38 | 110 | 209.9592 |  | 22.0918 | shared |  |  | 10.52% | 25 | 24.15%
Transmission Circuit 39 | 110 | 87.0702 |  | 17.3228 | shared |  | Normally open | 19.9% | 26 | 24.23%
Transmission Circuit 40 | 110 | 59.825 |  |  | shared |  | No 110kV VT at substation | 0% | 27 | 25.42%
Transmission Circuit 41 | 110 | 37.1525 |  |  | shared |  | No 110kV VT at substation | 0% | 28 | 25.58%
Transmission Circuit 42 | 110 | 37.1525 |  |  | shared |  | SCADA point records corrupted | 0% | 29 | 26.14%
Transmission Circuit 43 | 110 | 77.1629 |  | 11.5071 | shared |  |  | 14.91% | 30 | 26.29%
Transmission Circuit 44 | 110 | 77.1629 |  | 13.8979 | shared |  |  | 18.01% | 31 | 27.73%
Transmission Circuit 45 | 110 | 168.6151 |  | 109.3102 | shared |  |  | 64.83% | 32 | 28.31%
Transmission Circuit 46 | 110 | 168.6151 |  | 125.8694 | shared |  |  | 74.65% | 33 | 28.89%
Transmission Circuit 47 | 110 | 104.408 |  | 16.759 | shared |  |  | 16.05% | 34 | 29.29%
Transmission Circuit 48 | 110 | 104.408 |  | 20.0379 | shared |  | From 21/4/2011 only | 19.19% | 35 | 29.65%
Transmission Circuit 49 | 110 | 104.408 |  |  | shared |  | No 110kV VT at substation | 0% | 36 | 30.16%
Transmission Circuit 50 | 110 | 26.102 |  |  | shared |  | No 110kV VT at substation | 0% | 37 | 30.73%
Transmission Circuit 51 | 220 | 281.9779 |  | 107.7236 | shared | 1 |  | 38.2% | 38 | 31.95%
Transmission Circuit 52 | 220 | 281.9779 | yes | 97.1106 | shared | 1 |  | 34.44% | 39 | 34.06%
Transmission Circuit 53 | 220 | 281.9779 | yes | 104.1923 | shared | 1 |  | 36.95% | 40 | 34.44%
Transmission Circuit 54 | 220 | 334.1819 |  | 87.8528 | shared | 1 |  | 26.29% | 41 | 34.71%
Transmission Circuit 55 | 220 | 420 |  | 175.3629 | shared | 1 |  | 41.75% | 42 | 35.72%
Transmission Circuit 56 | 220 | 419.9184 |  | 97.2025 | shared | 1 |  | 23.15% | 43 | 36.95%
Transmission Circuit 57 | 220 | 419.9184 |  | 174.8374 | shared | 1 |  | 41.64% | 44 | 37.51%
Transmission Circuit 58 | 220 | 212.6266 |  | 87.5226 | shared |  |  | 41.16% | 45 | 38.2%
Transmission Circuit 59 | 110 | 104.408 |  | 92.1505 | shared |  |  | 88.26% | 46 | 40.55%
Transmission Circuit 60 | 110 | 99.4544 |  | 62.4767 | shared |  |  | 62.82% | 47 | 41.16%
Transmission Circuit 61 | 110 | 99.4544 |  | 62.2244 | shared |  |  | 62.57% | 48 | 41.63%
Transmission Circuit 62 | 110 | 118.888 |  | 8.2186 | shared |  |  | 6.913% | 49 | 41.64%
Transmission Circuit 63 | 110 | 155.6594 |  |  | shared |  | No 110kV VT at substation | 0% | 50 | 41.75%
Transmission Circuit 64 | 110 | 118.888 |  | 11.9947 | shared |  |  | 10.09% | 51 | 42.05%
Transmission Circuit 65 | 110 | 118.888 |  | 8.3912 | shared |  |  | 7.058% | 52 | 42.69%
Transmission Circuit 66 | 110 | 180.0467 |  |  | shared |  | Not commissioned in 2011 | 0% | 53 | 43.08%
Transmission Circuit 67 | 110 | 104.408 |  | 29.5573 | shared |  |  | 28.31% | 54 | 44.19%
Transmission Circuit 68 | 110 | 66.8745 |  | 68.645 | shared |  |  | 102.6% | 55 | 45.41%
Transmission Circuit 69 | 110 | 38.8672 |  | 6.724 | shared |  |  | 17.3% | 56 | 47.7%
Transmission Circuit 70 | 110 | 38.8672 |  | 17.1754 | shared |  |  | 44.19% | 57 | 48.42%
Transmission Circuit 71 | 220 | 281.9779 |  | 187.5156 | shared | 1 |  | 66.5% | 58 | 49.13%
Transmission Circuit 72 | 220 | 281.9779 |  | 183.7879 | shared | 1 |  | 65.18% | 59 | 50.1%
Transmission Circuit 73 | 110 | 77.925 |  | 50.7191 | shared | 1 | Winter 2011 data corrupted | 65.09% | 60 | 55.96%
Transmission Circuit 74 | 110 | 77.925 |  | 45.9982 | shared | 1 | Winter 2011 data corrupted | 59.03% | 61 | 57.61%
Transmission Circuit 75 | 220 | 238.538 | yes | 174.5559 | shared | 1 |  | 73.18% | 62 | 57.95%
Transmission Circuit 76 | 110 | 37.9146 |  | 5.7229 | shared |  |  | 15.09% | 63 | 58.17%
Transmission Circuit 77 | 220 | 138.3216 |  | 66.9734 | shared |  |  | 48.42% | 64 | 59.03%
Transmission Circuit 78 | 110 | 104.408 |  | 28.949 | shared |  |  | 27.73% | 65 | 62.14%
Transmission Circuit 79 | 110 | 117.3638 |  | 36.0643 | shared |  |  | 30.73% | 66 | 62.46%
Transmission Circuit 80 | 220 | 400.1037 | yes | 329.1689 | shared | 1 |  | 82.27% | 67 | 62.57%
Transmission Circuit 81 | 220 | 400.1037 | yes | 254.5559 | shared | 1 |  | 63.62% | 68 | 62.82%
Transmission Circuit 82 | 220 | 357.045 |  | 301.0615 | shared | 1 |  | 84.32% | 69 | 63.36%
Transmission Circuit 83 | 220 | 357.045 |  | 309.2089 | shared | 1 |  | 86.6% | 70 | 63.62%
Transmission Circuit 84 | 110 | 104.408 |  | 30.9552 | shared |  |  | 29.65% | 71 | 64.83%
Transmission Circuit 85 | 110 | 153.9447 |  | 21.7654 | shared |  |  | 14.14% | 72 | 65.09%
Transmission Circuit 86 | 110 | 153.9447 |  | 21.7978 | shared |  |  | 14.16% | 73 | 65.18%
Transmission Circuit 87 | 110 | 89.3565 |  | 40.5768 | shared |  |  | 45.41% | 74 | 66.5%
Transmission Circuit 88 | 110 | 381.0512 |  |  | shared |  | Not commissioned in 2011 | 0% | 75 | 73.05%
Transmission Circuit 89 | 110 | 74.686 |  | 59.7275 | shared |  |  | 79.97% | 76 | 73.18%
Transmission Circuit 90 | 110 | 74.686 |  | 61.7282 | shared |  |  | 82.65% | 77 | 74.65%
Transmission Circuit 91 | 110 | 74.686 |  | 71.9133 | shared |  |  | 96.29% | 78 | 75.55%
Transmission Circuit 92 | 110 | 74.686 |  | 56.4228 | shared |  |  | 75.55% | 79 | 79.97%
Transmission Circuit 93 | 110 | 74.686 |  | 67.5769 | shared |  |  | 90.48% | 80 | 80%
Transmission Circuit 94 | 110 | 140.7984 |  | 18.1865 | shared |  |  | 12.92% | 81 | 80.08%
Transmission Circuit 95 | 110 | 28.3883 |  | 0.23221 | shared |  |  | 0.818% | 82 | 82.27%
Transmission Circuit 96 | 110 | 28.3883 |  | 11.5102 | shared |  |  | 40.55% | 83 | 82.65%
Transmission Circuit 97 | 110 | 55.6335 |  | 40.6418 | shared |  |  | 73.05% | 84 | 84.32%
Transmission Circuit 98 | 110 | 55.6335 |  | 57.9735 | shared |  |  | 104.2% | 85 | 86.6%
Transmission Circuit 99 | 110 | 55.6335 |  | 44.5043 | shared |  |  | 80% | 86 | 88.26%
Transmission Circuit 100 | 110 | 55.6335 |  | 44.5487 | shared |  |  | 80.08% | 87 | 89.84%
Transmission Circuit 101 | 110 | 104.408 |  | 26.709 | shared |  |  | 25.58% | 88 | 90.48%
Transmission Circuit 102 | 110 | 130.3195 |  | 82.5653 | shared |  |  | 63.36% | 89 | 96.29%
Transmission Circuit 103 | 220 | 419.9184 | yes | 101.4222 | shared | 1 |  | 24.15% | 90 | 101.1%
Transmission Circuit 104 | 220 | 419.9184 | yes | 90.6038 | shared | 1 |  | 21.58% | 91 | 102.6%
Transmission Circuit 105 | 110 | 138.1311 | yes | 79.5717 | shared | 1 |  | 57.61% | 92 | 104.2%
[9 empty] | Mean | 44.34%
152.109